UTILITIES & MAINTENANCE DEPARTMENT

UTILITIES SERVICE

REQUEST FORM

In order to ensure that newly constructed building systems are ready for University provided utility services the following form and the associated specific System Request Forms must be completed and returned to the University of Notre Dame Utilities & Maintenance Department in order to schedule system checkout and service initiation.  Failure to provide this completed request may result in project schedule delays.  From the receipt of this form by the Notre Dame Utilities & Maintenance Department (David Brewton dbrewton@nd.edu) a service date will be scheduled within a maximum of two (2) weeks.  Systems are NOT to be operated using University produced utilities prior to system checkout.

Party Requesting Service:

Company Name:

Contact Person:

Telephone No.:

Date of Request:

Project Information:

Project:

Service Requested:

Steam and Condensate:				Domestic Cold Water:

Chilled Water:					Domestic Hot Water:

Electrical: 					Compressed Air:

Emergency Electrical:				Sanitary/Storm Sewers:

Service Details:

Requested Service Date:

Condition of Service:	  	 Complete 	 	 Partial

Define extent of Partial Service:

Contractor Sign-off:

We the following contractors do certify that all work will be complete by the requested service initiation date for the above mentioned system.  Such work shall include all necessary electrical work, mechanical piping, controls, etc. that is necessary to fully operate the aforementioned systems.  Complete applicable sections of checklist attached.

General Contractor:

Electrical Contractor:

Mechanical Contractor:

Temperature Control Contr.:

Utilities Services Initiation Schedule Information: (Completed by UND Utilities)

Scheduled Checkout Date:

Number of Days Scheduled On Site:

UTILITIES & MAINTENANCE DEPARTMENT

STEAM SERVICE

REQUEST FORM CHECKLIST

Building Envelope

| Item | Y/N |
| --- | --- |
| Building envelope enclosed |  |
| Permanent |  |
| Temporary |  |
| Mechanical room/tunnel secure with joint UND/MC locks |  |

If Temporary please explain means and methods:

Steam/Condensate System

| Item | Y/N |
| --- | --- |
| Condensate piping circuit complete using permanent components |  |
| System filled with treated condensate (no raw water) |  |
| Insulation complete |  |
| Gauges operational |  |
| Sample ports installed |  |
| Drains installed and closed |  |
| Overflow piping installed and open |  |
| Valves aligned for operation |  |
| Steam/condensate piping cleaned and flushed and prepped per specs |  |
| Steam/condensate piping pressure tested |  |
| Condensate meter installed |  |

Condensate Pump & Controls

| Item | Y/N |
| --- | --- |
| Discharge check valve installed |  |
| Condensate level probes installed |  |
| Pump motor rotation correct |  |
| Condensate pump panel rating matches motor HP and voltage |  |
| Condensate pump panel operational |  |
| Manual or automatic monitoring |  |

Contractor Representative:

UTILITIES & MAINTENANCE DEPARTMENT

CHILLED WATER SERVICE REQUEST FORM CHECKLIST

Building Envelope

| Item | Y/N |
| --- | --- |
| Building envelope enclosed |  |
| Permanent |  |
| Temporary |  |
| Mechanical Room secured with joint UND/MC locks |  |

If Temporary please explain means and methods:

Chilled Water System

| Item | Y/N |
| --- | --- |
| System filled with treated chilled water (no raw water) |  |
| Insulation complete |  |
| Gauges operational |  |
| Sample ports installed |  |
| Drains and vents installed and closed |  |
| Valves aligned for operation |  |
| Chilled water piping cleaned and treated per specs |  |
| Chilled water piping pressure tested |  |

Pump & Controls

| Item | Y/N |
| --- | --- |
| Pump motor rotation correct |  |
| Automatic controls operational |  |
| Manual or automatic monitoring |  |
| VFD Commissioning (performed by UND) |  |

Contractor Representative:

UTILITIES & MAINTENANCE DEPARTMENT

ELECTRICAL SERVICE

REQUEST FORM CHECKLIST

Building Envelope

| Item | Y/N |
| --- | --- |
| Main Electrical Room Watertight |  |
| Main Electrical Room secured with joint UND/EC locks |  |

Electrical System

| Item | Y/N |
| --- | --- |
| Grounding System complete (domestic/fire/structural/embedded electrode/etc) |  |
| Main Substation Equipment installed (by UND) |  |
| Metering operational (by UND) |  |
| Primary Feeder Installed and Tested (by UND) |  |
| Service Transformer Tested (by UND) |  |

Contractor Representative:

UTILITIES & MAINTENANCE DEPARTMENT

EMERGENCY ELECTRICAL SERVICE

REQUEST FORM CHECKLIST

Building Envelope

| Item | Y/N |
| --- | --- |
| Generator Room Watertight |  |
| Emergency Electrical Room secured with joint UND/EC locks |  |

Electrical System

| Item | Y/N |
| --- | --- |
| Generator properly grounded |  |
| CBAS Controls connected |  |
| ATS Controls connected |  |
| Battery and Charger installed and connected |  |

Mechanical System

| Item | Y/N |
| --- | --- |
| Generator and ATS(‘s) set and properly secured |  |
| Generator isolators installed |  |
| Exhaust Piping and insulation complete |  |
| Fuel and Vent Piping complete |  |
| Radiator Ductwork complete |  |
| Combustion Air System complete |  |
| Fuel Tank full |  |

Contractor Representative:

UTILITIES & MAINTENANCE DEPARTMENT

DOMESTIC COLD WATER SERVICE

REQUEST FORM CHECKLIST

Building Envelope

| Item | Y/N |
| --- | --- |
| Envelope Tempered to prevent freezing |  |
| Mechanical Room secured with joint UND/MC locks |  |

Domestic Cold Water System

| Item | Y/N |
| --- | --- |
| Piping complete |  |
| Insulation complete |  |
| Back Flow Preventer Installed and Tested (if applicable) |  |
| Piping Cleaned and Flushed and prepared per specifications |  |
| Pressure Tested |  |
| Drains Installed |  |
| Bacteria Testing complete |  |

Fire Protection Water System

| Item | Y/N |
| --- | --- |
| Piping complete |  |
| Double Check Valve Installed and Tested |  |
| Piping Cleaned and Flushed and prepared per specifications |  |
| Pressure Tested |  |
| Drains Installed |  |
| PIV installed connected to FAP |  |
| Flow and Tamper Switches monitored by FAP |  |
| Fire Pump and Controller Commissioned (if applicable) |  |
| Bacteria Testing complete |  |

Contractor Representative:

UTILITIES & MAINTENANCE DEPARTMENT

DOMESTIC HOT WATER SERVICE

REQUEST FORM CHECKLIST

Building Envelope

| Item | Y/N |
| --- | --- |
| Building Fully Enclosed and Heated |  |
| Mechanical Room secured with joint UND/MC locks |  |

Domestic Hot Water System

| Item | Y/N |
| --- | --- |
| Piping complete |  |
| Insulation complete |  |
| Back Flow Preventer Installed and Tested (if applicable) |  |
| Piping Cleaned and Flushed and prepared per specifications |  |
| Pressure Tested |  |
| Drains Installed |  |
| Recirculation Pump and Heater installed |  |
| CBAS monitoring installed |  |
| Gauges operational |  |
| Tempering valve installed and operational |  |

Contractor Representative:

UTILITIES & MAINTENANCE DEPARTMENT

COMPRESSED AIR SERVICE

REQUEST FORM CHECKLIST

Building Envelope

| Item | Y/N |
| --- | --- |
| Envelope Tempered to prevent freezing |  |
| Mechanical Room secured with joint UND/MC locks |  |

Compressed Air System

| Item | Y/N |
| --- | --- |
| Piping complete |  |
| Piping cleaned and prepared per specification |  |
| Pressure Tested |  |
| Pressure Regulator and Filters installed and tested |  |
| Air Dryer installed and operational |  |
| CBAS monitoring installed |  |
| Gauges operational |  |

Contractor Representative:

UTILITIES & MAINTENANCE DEPARTMENT

SEWER SERVICE

REQUEST FORM CHECKLIST

Building Envelope

| Item | Y/N |
| --- | --- |

Storm Sewer System

| Item | Y/N |
| --- | --- |
| Piping complete |  |
| Building Piping Cleaned and verified |  |
| Site underground piping cleaned and videotaped |  |
| Manholes and Catch Basins cleaned and inspected |  |
| Erosion Control and Illicit Discharge Permit in force |  |
| Erosion Control Measures in place (including, but not limited to) |  |
| Sediment/Erosion Fences/Inlet Filters |  |

Sanitary Sewer System

| Item | Y/N |
| --- | --- |
| Piping complete |  |
| Building Piping Cleaned of debris and verified |  |
| Site underground piping cleaned and videotaped |  |
| Manholes cleaned and inspected |  |

Contractor Representative: